## Modbusマップ
Modbus Func | Variable | Modbus Address (dec) | Beginning (HEX) | R/W | Content | Reference (Setting for Shipment)
Coil | CH1_HV | 1 | 0x0000 | R/W | High Voltage Power Supply ON/OFF | OFF
| CH2_HV | 2 | 0x0001 | R/W | High Voltage Power Supply ON/OFF | OFF
| CH3_HV | 3 | 0x0002 | R/W | High Voltage Power Supply ON/OFF | OFF
| CH4_HV | 4 | 0x0003 | R/W | High Voltage Power Supply ON/OFF | OFF
| CH5_HV | 5 | 0x0004 | R/W | High Voltage Power Supply ON/OFF | OFF
| CH6_HV | 6 | 0x0005 | R/W | High Voltage Power Supply ON/OFF | OFF
| CH7_HV | 7 | 0x0006 | R/W | High Voltage Power Supply ON/OFF | OFF
| CH8_HV | 8 | 0x0007 | R/W | High Voltage Power Supply ON/OFF | OFF
| CH1_RY | 9 | 0x0008 | R/W | High Pressure Relay ON/OFF | OFF
| CH2_RY | 10 | 0x0009 | R/W | High Pressure Relay ON/OFF | OFF
| CH3_RY | 11 | 0x000A | R/W | High Pressure Relay ON/OFF | OFF
| CH4_RY | 12 | 0x000B | R/W | High Pressure Relay ON/OFF | OFF
| CH5_RY | 13 | 0x000C | R/W | High Pressure Relay ON/OFF | OFF
| CH6_RY | 14 | 0x000D | R/W | High Pressure Relay ON/OFF | OFF
| CH7_RY | 15 | 0x000E | R/W | High Pressure Relay ON/OFF | OFF
| CH8_RY | 16 | 0x000F | R/W | High Pressure Relay ON/OFF | OFF
| CH1_0Adj | 17 | 0x0010 | R/W | 0Adj (Read=0、Write=1: 0AdjEXEC) | -
| CH2_0Adj | 18 | 0x0011 | R/W | 0Adj (Read=0、Write=1: 0AdjEXEC) | -
| CH3_0Adj | 19 | 0x0012 | R/W | 0Adj (Read=0、Write=1: 0AdjEXEC) | -
| CH4_0Adj | 20 | 0x0013 | R/W | 0Adj (Read=0、Write=1: 0AdjEXEC) | -
| CH5_0Adj | 21 | 0x0014 | R/W | 0Adj (Read=0、Write=1: 0AdjEXEC) | -
| CH6_0Adj | 22 | 0x0015 | R/W | 0Adj (Read=0、Write=1: 0AdjEXEC) | -
| CH7_0Adj | 23 | 0x0016 | R/W | 0Adj (Read=0、Write=1: 0AdjEXEC) | -
| CH8_0Adj | 24 | 0x0017 | R/W | 0Adj (Read=0、Write=1: 0AdjEXEC) | -
| Reserved | 25 | 0x0018 | R/W | Reserved Read=0、Write=No Impact | -
| Reserved | 26 | 0x0019 | R/W | Reserved Read=0、Write=No Impact | -
| Reserved | 27 | 0x001A | R/W | Reserved Read=0、Write=No Impact | -
| Reserved | 28 | 0x001B | R/W | Reserved Read=0、Write=No Impact | -
| Reserved | 29 | 0x001C | R/W | Reserved Read=0、Write=No Impact | -
| Reserved | 30 | 0x001D | R/W | Reserved Read=0、Write=No Impact | -
| Reserved | 31 | 0x001E | R/W | Reserved Read=0、Write=No Impact | -
| ALARM | 32 | 0x001F | R/W | ALARM CONNECTION POINT ON/OFF | OFF
Discrite | CH1_Detect | 10001 | 0x0000 | RO | DISCONNECTED=0 DETECTION=1 | CURRENT VALUE
| CH2_Detect | 10002 | 0x0001 | RO | DISCONNECTED=0 DETECTION=1 | CURRENT VALUE
| CH3_Detect | 10003 | 0x0002 | RO | DISCONNECTED=0 DETECTION=1 | CURRENT VALUE
| CH4_Detect | 10004 | 0x0003 | RO | DISCONNECTED=0 DETECTION=1 | CURRENT VALUE
| CH5_Detect | 10005 | 0x0004 | RO | DISCONNECTED=0 DETECTION=1 | CURRENT VALUE
| CH6_Detect | 10006 | 0x0005 | RO | DISCONNECTED=0 DETECTION=1 | CURRENT VALUE
| CH7_Detect | 10007 | 0x0006 | RO | DISCONNECTED=0 DETECTION=1 | CURRENT VALUE
| CH8_Detect | 10008 | 0x0007 | RO | DISCONNECTED=0 DETECTION=1 | CURRENT VALUE
| CH1_Pulse | 10009 | 0x0008 | RO | PULSE=0 DETECTION=1 | CURRENT VALUE
| CH2_Pulse | 10010 | 0x0009 | RO | PULSE=0 DETECTION=1 | CURRENT VALUE
| CH3_Pulse | 10011 | 0x000A | RO | PULSE=0 DETECTION=1 | CURRENT VALUE
| CH4_Pulse | 10012 | 0x000B | RO | PULSE=0 DETECTION=1 | CURRENT VALUE
| CH5_Pulse | 10013 | 0x000C | RO | PULSE=0 DETECTION=1 | CURRENT VALUE
| CH6_Pulse | 10014 | 0x000D | RO | PULSE=0 DETECTION=1 | CURRENT VALUE
| CH7_Pulse | 10015 | 0x000E | RO | PULSE=0 DETECTION=1 | CURRENT VALUE
| CH8_Pulse | 10016 | 0x000F | RO | PULSE=0 DETECTION=1 | CURRENT VALUE
Read Input | CH1_StaticElec | 30001 | 0x0000 | RO | CH1 Static Electricity Level Float(32ibt) kV unit | Disconnection is NaN Response
| CH1_StaticElec | 30002 | 0x0001 | RO
| CH2_StaticElec | 30003 | 0x0002 | RO | CH1 Static Electricity Level Float(32ibt) kV unit | Disconnection is NaN Response
| CH2_StaticElec | 30004 | 0x0003 | RO
| CH3_StaticElec | 30005 | 0x0004 | RO | CH1 Static Electricity Level Float(32ibt) kV unit | Disconnection is NaN Response
| CH3_StaticElec | 30006 | 0x0005 | RO
| CH4_StaticElec | 30007 | 0x0006 | RO | CH1 Static Electricity Level Float(32ibt) kV unit | Disconnection is NaN Response
| CH4_StaticElec | 30008 | 0x0007 | RO
| CH5_StaticElec | 30009 | 0x0008 | RO | CH1 Static Electricity Level Float(32ibt) kV unit | Disconnection is NaN Response
| CH5_StaticElec | 30010 | 0x0009 | RO
| CH6_StaticElec | 30011 | 0x000A | RO | CH1 Static Electricity Level Float(32ibt) kV unit | Disconnection is NaN Response
| CH6_StaticElec | 30012 | 0x000B | RO
| CH7_StaticElec | 30013 | 0x000C | RO | CH1 Static Electricity Level Float(32ibt) kV unit | Disconnection is NaN Response
| CH7_StaticElec | 30014 | 0x000D | RO
| CH8_StaticElec | 30015 | 0x000E | RO | CH1 Static Electricity Level Float(32ibt) kV unit | Disconnection is NaN Response
| CH8_StaticElec | 30016 | 0x000F | RO
| Temperture Sensor | 30017 | 0x0010 | RO | Temperture Sensor Float(32ibt) Celsius unit | Disconnection is NaN Response
| Temperture Sensor | 30018 | 0x0011 | RO
| Humidity Sensor | 30019 | 0x0012 | RO | Humidity Sensor Float(32ibt) % unit | Disconnection is NaN Response
| Humidity Sensor | 30020 | 0x0013 | RO
| Status | 30021 | 0x0014 | RO | Status | CURRENT VALUE
| Meas CH | 30022 | 0x0015 | RO | CH1～CH8 Effective Measurement in CH shows in Binary form. CH8 : bit7～CH1 : bit0 | Caculated Numeric Expression in CH
| Range | 30023 | 0x0016 | RO | 1～4 : Range Setting by Caculated Static Electricity Level レンジ1 : 1.9kV Scale レンジ2 : 19kV Scale レンジ3 : 0.5kV Scale レンジ4 : 0.2kV Scale | Effective Range by Caculated Numeric Expression
| CH Status | 30024 | 0x0017 | RO | CH1～CH8 Detected Connection Shows In Binary Form。 CH8 : bit7～CH1 : bit0 Connection Point ON/OFF equivalents to Binary number | Connected CH
| CH Pulse | 30025 | 0x0018 | RO | CH1～CH8の Detected Paulse shows in Binary form。 CH8 : bit7～CH1 : bit0 Connection Point ON/OFF equivalents to Binary number | Paulse CH
| Reserved | 30026 | 0x0019 | - | Reserved No Access | -
| Reserved | 30027 | 0x001A | - | Reserved No Access | -
| Reserved | 30028 | 0x001B | - | Reserved No Access | -
| Reserved | 30029 | 0x001C | - | Reserved No Access | -
| Reserved | 30030 | 0x001D | - | Reserved No Access | -
| Version | 30031 | 0x001E | RO | Version No X.Y.ZZ(HEX) | Firmware Version
| Uptime | 30032 | 0x001F | RO | Working Time (ms) (unssigend long 32bit) | 0
| Uptime | 30033 | 0x0020 | RO | Working Time (ms) (unssigend long 32bit) | 0
| CH1_Raw | 30101 | 0x0064 | RO | CH1 AD Smooth Value | Disconnect CH is 0x8000
| CH2_Raw | 30102 | 0x0065 | RO | CH2 AD Smooth Value | Disconnect CH is 0x8000
| CH3_Raw | 30103 | 0x0066 | RO | CH3 AD Smooth Value | Disconnect CH is 0x8000
| CH4_Raw | 30104 | 0x0067 | RO | CH4 AD Smooth Value | Disconnect CH is 0x8000
| CH5_Raw | 30105 | 0x0068 | RO | CH5 AD Smooth Value | Disconnect CH is 0x8000
| CH6_Raw | 30106 | 0x0069 | RO | CH6 AD Smooth Value | Disconnect CH is 0x8000
| CH7_Raw | 30107 | 0x006A | RO | CH7 AD Smooth Value | Disconnect CH is 0x8000
| CH8_Raw | 30108 | 0x006B | RO | CH8 AD Smooth Value | Disconnect CH is 0x8000
| CH1_0Adj | 30109 | 0x006C | RO | CH1 0 AdjSet Value | Disconnect CH is 0x8000
| CH2_0Adj | 30110 | 0x006D | RO | CH2 0 AdjSet Value | Disconnect CH is 0x8000
| CH3_0Adj | 30111 | 0x006E | RO | CH3 0 AdjSet Value | Disconnect CH is 0x8000
| CH4_0Adj | 30112 | 0x006F | RO | CH4 0 AdjSet Value | Disconnect CH is 0x8000
| CH5_0Adj | 30113 | 0x0070 | RO | CH5 0 AdjSet Value | Disconnect CH is 0x8000
| CH6_0Adj | 30114 | 0x0071 | RO | CH6 0 AdjSet Value | Disconnect CH is 0x8000
| CH7_0Adj | 30115 | 0x0072 | RO | CH7 0 AdjSet Value | Disconnect CH is 0x8000
| CH8_0Adj | 30116 | 0x0073 | RO | CH8 0 AdjSet Value | Disconnect CH is 0x8000
| R-SW | 30117 | 0x0074 | RO | Rotary SW | CURRENT VALUE
| DIPSW | 30118 | 0x0075 | RO | DIP Switch | CURRENT VALUE
Holding | Alarm | 40001 | 0x0000 | R/W | Specify ALARM CONNECTION POINT ON/OFF with Binary。 | 0 : OFF
| HV ON/OFF | 40002 | 0x0001 | R/W | Specify CH1～CH8のHV ON/OFF with Binary。 | Equivalents to Coil
| HV Relay | 40003 | 0x0002 | R/W | Specity CH1～CH8のHV Relay ON/OFF with Binary。 | Equivalents to Coil
| 0Adj | 40004 | 0x0003 | R/W | Specify 0Adj CH1～CH8 with Binary。 | Equivalents to Coil | ※ 2018/10/1 additional
| Reserved | 40005 | 0x0004 | - | Reserved No Access | -
| Reserved | 40006 | 0x0005 | - | Reserved No Access | -
| Reserved | 40007 | 0x0006 | - | Reserved No Access | -
| Reserved | 40008 | 0x0007 | - | Reserved No Access | -
| Reserved | 40009 | 0x0008 | - | Reserved No Access | -
| Reserved | 40010 | 0x0009 | - | Reserved No Access | -
| IP Address | 40011 | 0x000A | R/W | Specify IPv4 address setting with 32bit value | 0xC0A8 (192.168)
| IP Address | 40012 | 0x000B | R/W |  | 0x0001 (0.1)
| Subnet Mask | 40013 | 0x000C | R/W | Specify Subnet Mask Setting with 32but value | 0xFFFF (255.255)
| Subnet Mask | 40014 | 0x000D | R/W |  | 0xFF00 (255.0)
| Gateway | 40015 | 0x000E | R/W | Specify Default Gateway Setting with 32but value | 0xC0A8 (192.168)
| Gateway | 40016 | 0x000F | R/W |  | 0x0001 (0.1)
| Service Port | 40017 | 0x0010 | R/W | Modbus TCP Service Support | 502
| DHCP | 40018 | 0x0011 | R/W | Use / No Use DHCP 1/0 specification | 0
| Network Write Enable | 40019 | 0x0012 | R/W | Instruct Entry on IP Setting Specified each setting item by Write, then keep non-volatility on this registration by the entry of 0x4e6e 。 Disconnected when connecting to Modbus TCP。 Network is innitilized after set-up。 0 for Read | -
| Reserved | 40020 | 0x0013 | - | Reserved No Access | -
| Serial Baud | 40021 | 0x0014 | R/W | ModbusRTU Bit Rate 4800/9600/19200/38400 | 9600
| Serial Baud | 40022 | 0x0015 | R/W
| Stop bit | 40023 | 0x0016 | R/W | Stop Bit Length 1 : 1Stop 2 : 2Stop | 1 : 1Stop
| Parity | 40024 | 0x0017 | R/W | Parity Setting 0: None 1:Odd 2:Even | 2 : Even
| Delay Time | 40025 | 0x0018 | R/W | Modbus RTU Delayed Response (ms) | 0
| Serial Write Enable | 40026 | 0x0019 | R/W | Instruct Entry on Serial Setting Specified each setting item by Write, then keep non-volatility on this registration by the entry of 0x4e6e 。 Disconnected when connecting to Modbus TCP。 Network is innitilized after set-up。 0 for Read | -
| Reserved | 40027 | 0x001A | - | Reserved No Access | -
| Reserved | 40028 | 0x001B | - | Reserved No Access | -
| Reserved | 40029 | 0x001C | - | Reserved No Access | -
| Reserved | 40030 | 0x001D | - | Reserved No Access | -
| Factory Init | 40031 | 0x001E | R/W | Enter 0x00ff on this registration at Shipment Setting Reset each setting on Network/Serial at Shipment Condition 。 Reset 0Adj value to Default (0x8000)。 0 Response when Read on Registraion. Disconnect Modbus RTU/TCP after setting。 | -
| System Reset | 40032 | 0x001F | R/W | Restart Firmware on this registration by entry of 0x00ff。 0 Response when Read on Registraion. Disconnect Modbus RTU/TCP 。 | -

## Q&A
STT | Ngày tạo | Người tạo | Nội dung câu hỏi | Ngày trả lời | Người trả lời | Nội dung trả lời
1 | 2020-11-16 | Khoi-AKB | Tôi muốn hỏi về lệnh phóng điện Theo mô tả trong sheet [Modbusマップ] thì tôi hiểu để phóng điện thì cần gọi lệnh "HV ON/OFF" tại dòng 102, sau đó gọi lệnh "HV Relay" tại dòng 103 - Đối với lệnh "HV ON/OFF" tại dòng 102, tham số truyền dựa theo mô tả từ dòng số 2 đến dòng số 9 - Đối với lệnh "HV Relay" tại dòng 103, tham số truyền dựa theo mô tả từ dòng số 10 đến dòng số 17 Hiện tại tôi cũng chỉ phán đoán như vậy còn không chắc chắn là đúng hay sai, tôi không hiểu giá trị cột [Modbus アドレス(dec)], cột [開始アドレス(HEX)] mô tả tham số gì trong lệnh phóng điện Nhờ các bạn giải thích giúp tôi